## 119_152
S&C Power Fuses - Type SMD-2C (34.5 and 46 kV) | [9 empty] | S&C Power Fuses - Type SMD-2C (34.5 and 46 kV) | [9 empty] | S&C Power Fuses - Type SMD-2C (34.5 and 46 kV) | [9 empty] | S&C Power Fuses - Type SMD-2C (34.5 and 46 kV)
Slow Speed (TCC 119-1-5-2) | [9 empty] | Slow Speed (TCC 119-1-5-2) | [9 empty] | Slow Speed (TCC 119-1-5-2) | [9 empty] | Slow Speed (TCC 119-1-5-2)
Total Clearing Time-Current Characteristic Curves Dated August 29, 1988 | [9 empty] | Total Clearing Time-Current Characteristic Curves Dated August 29, 1988 | [9 empty] | Total Clearing Time-Current Characteristic Curves Dated August 29, 1988 | [9 empty] | Total Clearing Time-Current Characteristic Curves Dated August 29, 1988
Tolerance: Curves are plotted to maximum test points. All variations are minus. | [9 empty] | Tolerance: Curves are plotted to maximum test points. All variations are minus. | [9 empty] | Tolerance: Curves are plotted to maximum test points. All variations are minus. | [9 empty] | Tolerance: Curves are plotted to maximum test points. All variations are minus.
15E |  | 20E |  | 25E |  | 30E |  | 40E |  | 50E |  | 65E |  | 80E |  | 100E |  | 125E |  | 150E |  | 175E |  | 200E |  | 250E |  | 300E |  | 2-200E |  | 2-250E |  | 2-300E
Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time
42998.7 | 0.016307 | 42998.7 | 0.016307 | 42998.7 | 0.016307 | 42998.7 | 0.016307 | 42998.7 | 0.016405 | 42998.7 | 0.016405 | 42998.7 | 0.016405 | 42998.7 | 0.016504 | 42998.7 | 0.016603 | 42849.3 | 0.01668 | 42873.8 | 0.025369 | 43046 | 0.025559 | 43095.4 | 0.025735 | 43070.7 | 0.026468 | 43046 | 0.031359 | 43021.4 | 0.032943 | 43046 | 0.035899 | 43046 | 0.040327
41065.6 | 0.016703 | 41354 | 0.016603 | 41519.8 | 0.016603 | 40575.7 | 0.016803 | 41478.3 | 0.016603 | 40779.1 | 0.016803 | 41519.8 | 0.016703 | 41478.3 | 0.016803 | 40292.7 | 0.017092 | 38785.8 | 0.017432 | 38763.6 | 0.026911 | 35797.8 | 0.028613 | 39255 | 0.027315 | 40348.9 | 0.027932 | 36943.1 | 0.033514 | 39097.9 | 0.03433 | 40907.2 | 0.036816 | 40837 | 0.041929
39653.1 | 0.016888 | 39891.8 | 0.016888 | 40091.7 | 0.016888 | 39141 | 0.017092 | 40051.7 | 0.016888 | 39376.5 | 0.017092 | 40091.7 | 0.016989 | 40051.7 | 0.017092 | 38829.1 | 0.017402 | 34038.6 | 0.018662 | 32945.5 | 0.029715 | 27398 | 0.033803 | 34470.1 | 0.029818 | 34767.5 | 0.031377 | 30722.5 | 0.037133 | 33497.2 | 0.038016 | 37261.8 | 0.039278 | 36355.5 | 0.046218
38212.8 | 0.017194 | 38481.2 | 0.017194 | 38674.1 | 0.017092 | 37719.2 | 0.017298 | 38596.8 | 0.017194 | 37946.2 | 0.017402 | 38674.1 | 0.017298 | 38635.4 | 0.017402 | 37418.7 | 0.017789 | 29279.7 | 0.020185 | 27148.2 | 0.033266 | 23179.4 | 0.037669 | 29992.4 | 0.032363 | 29566.1 | 0.035207 | 26291.4 | 0.040979 | 28962.9 | 0.042582 | 32458.7 | 0.043895 | 32964.4 | 0.050946
36787.9 | 0.017489 | 37046.4 | 0.017489 | 37232.1 | 0.017402 | 36276.5 | 0.0177 | 37157.7 | 0.017489 | 36494.8 | 0.0177 | 37232.1 | 0.017594 | 37194.8 | 0.0177 | 35987.4 | 0.018094 | 25418 | 0.021771 | 22512.3 | 0.037197 | 18099.6 | 0.043221 | 25725.5 | 0.035715 | 24743 | 0.039572 | 21492 | 0.047208 | 24363.4 | 0.049027 | 28307 | 0.049507 | 29112.5 | 0.057756
35345.5 | 0.017789 | 35629.4 | 0.017789 | 35808 | 0.0177 | 34854.1 | 0.018004 | 35736.4 | 0.017789 | 35063.8 | 0.018004 | 35808 | 0.017896 | 35772.2 | 0.018004 | 34541.8 | 0.018497 | 22192.3 | 0.023481 | 18678.8 | 0.041214 | 15000.3 | 0.048026 | 21864.4 | 0.039345 | 20635.7 | 0.044046 | 17822 | 0.054979 | 21222.9 | 0.055358 | 24210.5 | 0.057723 | 26231.3 | 0.064656
33925.6 | 0.018203 | 34198.1 | 0.018094 | 34369.5 | 0.018094 | 33420.5 | 0.018294 | 34300.8 | 0.018094 | 33655.3 | 0.018294 | 34369.5 | 0.018203 | 34335.2 | 0.018294 | 33121.1 | 0.018795 | 18700.2 | 0.02578 | 15260.2 | 0.045927 | 12741.6 | 0.052727 | 18016.9 | 0.044147 | 17368.6 | 0.049677 | 15613.8 | 0.061583 | 17689.8 | 0.066421 | 20969.2 | 0.067109 | 23743.7 | 0.072547
32497.7 | 0.018497 | 32758.7 | 0.018497 | 32955.9 | 0.018404 | 31981.9 | 0.018701 | 32890 | 0.018497 | 32206.6 | 0.018701 | 32923 | 0.018608 | 32890 | 0.018701 | 31695.4 | 0.019309 | 15966.4 | 0.028303 | 12553.3 | 0.050887 | 10885.2 | 0.058388 | 15578.1 | 0.048496 | 14643.9 | 0.056609 | 13500.3 | 0.070498 | 14948.9 | 0.079876 | 18193.2 | 0.07838 | 21615.4 | 0.081354
31067.7 | 0.018908 | 31317.3 | 0.018795 | 31537.3 | 0.018795 | 30574.6 | 0.019098 | 31442.8 | 0.018908 | 30789.4 | 0.019098 | 31505.7 | 0.018908 | 31474.3 | 0.019098 | 30270.4 | 0.019699 | 13718.5 | 0.031109 | 10854.1 | 0.0552 | 9352.67 | 0.065551 | 13539 | 0.052909 | 12241 | 0.065739 | 11606.2 | 0.082386 | 12524.6 | 0.099247 | 15649.6 | 0.093774 | 19265.4 | 0.094964
29611.7 | 0.019309 | 29909.3 | 0.019213 | 30089.3 | 0.019213 | 29141.7 | 0.019503 | 30029.2 | 0.019213 | 29346.4 | 0.019503 | 30089.3 | 0.019406 | 30059.2 | 0.019503 | 28822.9 | 0.020198 | 11834.3 | 0.034134 | 9444.16 | 0.060016 | 7862.92 | 0.076036 | 11814 | 0.058221 | 10457.5 | 0.075819 | 10035.1 | 0.097444 | 10748.9 | 0.12149 | 14052.4 | 0.10852 | 16907.4 | 0.11414
28195.7 | 0.019699 | 28479.1 | 0.019582 | 28679.1 | 0.019582 | 27692.7 | 0.019897 | 28593.2 | 0.019699 | 27915.2 | 0.019897 | 28650.5 | 0.019798 | 28621.8 | 0.019997 | 27417.2 | 0.020689 | 10368.1 | 0.037283 | 8312.02 | 0.066345 | 6802.46 | 0.087244 | 10308.9 | 0.065251 | 9358.03 | 0.084441 | 8786.76 | 0.11539 | 9262.07 | 0.14915 | 12053.2 | 0.13531 | 15017.5 | 0.13585
26767 | 0.020097 | 27036 | 0.020097 | 27225.9 | 0.019997 | 26263.2 | 0.020299 | 27171.5 | 0.020097 | 26500.7 | 0.020401 | 27225.9 | 0.020198 | 27171.5 | 0.020401 | 25975.9 | 0.021191 | 8651.96 | 0.042534 | 7137.66 | 0.075732 | 6160.89 | 0.096168 | 8637.11 | 0.076123 | 7944.38 | 0.1019 | 7566.97 | 0.14165 | 8105.21 | 0.18091 | 10596.1 | 0.16328 | 13500.3 | 0.16022
25334.6 | 0.020606 | 25614.8 | 0.020503 | 25794.7 | 0.020503 | 24832.9 | 0.020792 | 25743.2 | 0.020606 | 25057.4 | 0.020897 | 25794.7 | 0.020689 | 25743.2 | 0.021001 | 24536.7 | 0.021815 | 7137.66 | 0.049394 | 6206.92 | 0.086745 | 5317.79 | 0.11258 | 7361.81 | 0.089011 | 7016.09 | 0.11956 | 6471.88 | 0.17947 | 7307.21 | 0.21154 | 9640.87 | 0.1895 | 12332.5 | 0.18436
23907 | 0.021107 | 24171.4 | 0.021001 | 24365.5 | 0.021001 | 23410.2 | 0.021404 | 24316.9 | 0.021107 | 23621.8 | 0.021404 | 24365.5 | 0.021297 | 24316.9 | 0.021511 | 23107.8 | 0.022412 | 5949.4 | 0.058054 | 5326.93 | 0.10166 | 4674.94 | 0.13126 | 6442.3 | 0.10313 | 5864.84 | 0.15234 | 5570.25 | 0.22842 | 6644.62 | 0.24566 | 8761.64 | 0.22108 | 11375.9 | 0.21154
22469.7 | 0.021706 | 22741 | 0.021598 | 22946.6 | 0.021511 | 21980.8 | 0.021902 | 22877.9 | 0.021706 | 22201.7 | 0.022012 | 22923.7 | 0.021815 | 22900.8 | 0.0221 | 21675.2 | 0.023094 | 5419.23 | 0.064103 | 4608.5 | 0.11983 | 4171.46 | 0.15217 | 5605.44 | 0.12191 | 5068.05 | 0.18799 | 4927.83 | 0.27961 | 6024.83 | 0.28906 | 7939.83 | 0.26223 | 10209 | 0.25541
21034.6 | 0.0223 | 21309.9 | 0.022211 | 21524 | 0.0221 | 20556.3 | 0.022502 | 21438.1 | 0.022211 | 20762.9 | 0.022705 | 21502.5 | 0.022502 | 21459.6 | 0.022796 | 20250.3 | 0.023893 | 4726.08 | 0.074484 | 4056.04 | 0.141 | 3703.06 | 0.17947 | 4925.01 | 0.14378 | 4339.57 | 0.23913 | 4229.18 | 0.36496 | 5299.55 | 0.36122 | 7109.11 | 0.31936 | 9230.3 | 0.30575
19612.6 | 0.022887 | 19889.1 | 0.022796 | 20088.9 | 0.022705 | 19128.3 | 0.023187 | 20008.8 | 0.022887 | 19339.9 | 0.023397 | 20068.9 | 0.023094 | 20028.8 | 0.02349 | 18824.7 | 0.024794 | 4138.15 | 0.087745 | 3569.81 | 0.16793 | 3323.22 | 0.20961 | 4417.3 | 0.16793 | 3700.94 | 0.31123 | 3786.69 | 0.44447 | 4723.38 | 0.44574 | 6398.18 | 0.38648 | 8470.58 | 0.35752
18177.2 | 0.023584 | 18451.9 | 0.02349 | 18656 | 0.023397 | 17693 | 0.023989 | 18581.6 | 0.023584 | 17906.6 | 0.024109 | 18637.4 | 0.023893 | 18600.1 | 0.024303 | 17394.8 | 0.025805 | 3582.09 | 0.10607 | 3120.35 | 0.20311 | 2956.83 | 0.25078 | 3910.08 | 0.20079 | 3165.34 | 0.406 | 3351.89 | 0.5567 | 4154.77 | 0.5657 | 5738.6 | 0.4723 | 7858.42 | 0.41115
16746.2 | 0.0244 | 17033.3 | 0.024303 | 17221.7 | 0.024206 | 16267.5 | 0.024794 | 17152.9 | 0.0244 | 16480.4 | 0.024993 | 17204.5 | 0.024695 | 17170.1 | 0.025194 | 15961.3 | 0.026886 | 3097.21 | 0.13171 | 2773.15 | 0.24258 | 2623.32 | 0.30383 | 3413.87 | 0.24693 | 2743.15 | 0.5236 | 3001.19 | 0.6917 | 3684.03 | 0.71139 | 5158.82 | 0.57617 | 7195.11 | 0.48491
15320.2 | 0.025194 | 15598.4 | 0.025093 | 15802.5 | 0.024993 | 14837.7 | 0.025702 | 15723.7 | 0.025295 | 15046.9 | 0.026013 | 15770.9 | 0.025702 | 15739.4 | 0.0263 | 14529.3 | 0.028292 | 2670.3 | 0.1662 | 2442.11 | 0.29627 | 2334.1 | 0.36812 | 2997.75 | 0.30314 | 2354.23 | 0.69528 | 2690.26 | 0.85895 | 3201.8 | 0.92961 | 4605.86 | 0.71384 | 6561.43 | 0.58381
13890 | 0.026222 | 14170.6 | 0.026013 | 14370.4 | 0.025909 | 13398.9 | 0.026698 | 14298.7 | 0.0263 | 13628.6 | 0.027101 | 14341.7 | 0.026778 | 14313 | 0.027484 | 13107.3 | 0.029922 | 2396.4 | 0.19896 | 2127.32 | 0.373 | 2095.88 | 0.4432 | 2584.55 | 0.38848 | 2120.02 | 0.84965 | 2488.7 | 1.0049 | 2834.16 | 1.1872 | 4150.01 | 0.86934 | 6069.84 | 0.67875
12468 | 0.027292 | 12732.6 | 0.027101 | 12938 | 0.026993 | 11967.2 | 0.027899 | 12860.6 | 0.027401 | 12196.7 | 0.028292 | 12912.2 | 0.028011 | 12886.4 | 0.028893 | 11671.7 | 0.031899 | 2064.91 | 0.25688 | 1858.41 | 0.46879 | 1856.28 | 0.55162 | 2279.94 | 0.48241 | 1904.74 | 1.0419 | 2251.4 | 1.238 | 2488.7 | 1.5523 | 3688.25 | 1.109 | 5494.22 | 0.82755
11036.1 | 0.028491 | 11304.1 | 0.028292 | 11509.5 | 0.028207 | 10539.9 | 0.0293 | 11440.6 | 0.028691 | 10763.6 | 0.029802 | 11486.5 | 0.029506 | 11452 | 0.030618 | 10248.9 | 0.034418 | 1824.67 | 0.31699 | 1630.95 | 0.58784 | 1641.26 | 0.69528 | 2007.77 | 0.60666 | 1695.71 | 1.3109 | 1958.94 | 1.6542 | 2219.4 | 1.9848 | 3313.72 | 1.3716 | 5018.96 | 0.99008
9603.93 | 0.030012 | 9876.64 | 0.029802 | 10076.1 | 0.029594 | 9108.18 | 0.030895 | 10005.8 | 0.030313 | 9329.42 | 0.031677 | 10056 | 0.031299 | 10025.9 | 0.032707 | 8812.51 | 0.037811 | 1593.11 | 0.40484 | 1485.61 | 0.69448 | 1475.44 | 0.85453 | 1755.99 | 0.78416 | 1483.91 | 1.7558 | 1759.01 | 2.1395 | 1991.74 | 2.5407 | 2975.52 | 1.7348 | 4726.08 | 1.1205
8175.75 | 0.031677 | 8450.05 | 0.031487 | 8646.66 | 0.031299 | 7684.25 | 0.032904 | 8577.76 | 0.032188 | 7902.45 | 0.034008 | 8629.38 | 0.033501 | 8594.93 | 0.035502 | 7382.95 | 0.042674 | 1386.16 | 0.51912 | 1342.42 | 0.83135 | 1350.9 | 1.0183 | 1580.39 | 0.96378 | 1315.03 | 2.3129 | 1573.16 | 2.8054 | 1830.95 | 3.1173 | 2662.67 | 2.2309 | 4407.19 | 1.2908
6740.76 | 0.033906 | 7015.86 | 0.033602 | 7215.08 | 0.033301 | 6253.7 | 0.035431 | 7143.29 | 0.034625 | 6469.98 | 0.03721 | 7200.66 | 0.036583 | 7164.75 | 0.039393 | 7265.76 | 0.043189 | 1253.27 | 0.62679 | 1229.81 | 0.98386 | 1213.03 | 1.2805 | 1442.03 | 1.1603 | 1180.14 | 3.0189 | 1428.06 | 3.585 | 1664.92 | 4.0433 | 2400.52 | 2.8573 | 4012.15 | 1.5856
5313.09 | 0.036583 | 5585.49 | 0.036183 | 5784.45 | 0.036002 | 4821.92 | 0.039001 | 5715.45 | 0.037886 | 5043.87 | 0.041997 | 5767.12 | 0.041001 | 5732.62 | 0.045403 | 6980.86 | 0.044504 | 1092.97 | 0.81859 | 1089.85 | 1.2572 | 1109.37 | 1.5506 | 1289.67 | 1.455 | 1074.97 | 3.8401 | 1306.02 | 4.4671 | 1512.22 | 5.3721 | 2221.94 | 3.4818 | 3671.39 | 1.9332
3885.19 | 0.040512 | 4154.42 | 0.040028 | 4354.34 | 0.03959 | 3391.16 | 0.044594 | 4285.22 | 0.043103 | 3611.68 | 0.050582 | 4336.96 | 0.048501 | 5524.39 | 0.046506 | 6640.4 | 0.046228 | 965.263 | 1.0533 | 959.752 | 1.6307 | 1016.89 | 1.8883 | 1131.18 | 1.9255 | 996.147 | 4.7468 | 1207.48 | 5.6823 | 1394.12 | 7.1827 | 2060.18 | 4.2719 | 3392.44 | 2.3368
2452.66 | 0.046693 | 2726.92 | 0.045998 | 2924.64 | 0.045585 | 1960.45 | 0.057489 | 2855.29 | 0.053228 | 3533.09 | 0.051192 | 4263.85 | 0.049087 | 5286.59 | 0.048067 | 6335.53 | 0.047923 | 865.756 | 1.3452 | 867.244 | 2.0332 | 920.987 | 2.3597 | 993.868 | 2.6401 | 920.987 | 5.9557 | 1095.48 | 8.0225 | 1322.58 | 9.0897 | 1917.87 | 5.2025 | 3154.49 | 2.7862
1023.44 | 0.064689 | 1295.86 | 0.06209 | 1495.07 | 0.060497 | 1921.63 | 0.058067 | 2779.23 | 0.054141 | 3421.82 | 0.052279 | 4113.08 | 0.050279 | 5038.83 | 0.049679 | 5848.43 | 0.051192 | 775.173 | 1.7318 | 772.515 | 2.6507 | 830.787 | 3.0397 | 880.253 | 3.618 | 839.876 | 8.232 | 1005.89 | 11.281 | 1248.97 | 11.9188 | 1798.73 | 6.3758 | 2863.52 | 3.5768
969.646 | 0.06626 | 1233.89 | 0.063598 | 1456.7 | 0.061411 | 1844.43 | 0.059477 | 2654.28 | 0.055623 | 3261.45 | 0.053925 | 3955.76 | 0.051603 | 4788.29 | 0.051707 | 5496.84 | 0.054141 | 682.247 | 2.3489 | 701.661 | 3.3622 | 745.143 | 4.0294 | 777.396 | 5.2144 | 780.965 | 11.2939 | 951.543 | 14.9113 | 1186.24 | 15.8994 | 1694.74 | 7.8903 | 2670.3 | 4.3137
886.19 | 0.069518 | 1144.73 | 0.06626 | 1374.61 | 0.063345 | 1763.27 | 0.061105 | 2514.75 | 0.057489 | 3074.59 | 0.056069 | 3740.33 | 0.053709 | 4500.43 | 0.054304 | 5171.55 | 0.056974 | 605.641 | 3.1695 | 639.866 | 4.2597 | 683.42 | 5.0585 | 717.918 | 6.7094 | 734.972 | 15.6554 | 914.68 | 18.2325 | 1146.17 | 19.9256 | 1594.02 | 10.2048 | 2475.91 | 5.3814
820.514 | 0.0725 | 1060.96 | 0.069172 | 1294.56 | 0.06547 | 1668.91 | 0.063218 | 2377.79 | 0.059596 | 2912.97 | 0.058299 | 3543.71 | 0.05579 | 4242.59 | 0.057088 | 4831.58 | 0.0608 | 537.944 | 4.3261 | 585.521 | 5.459 | 636.212 | 6.2385 | 663.75 | 8.7324 | 703.673 | 20.0861 | 871.226 | 23.88 | 1097.99 | 27.1187 | 1516.55 | 12.9958 | 2338.11 | 6.453
765.808 | 0.075459 | 975.481 | 0.072937 | 1191.45 | 0.068827 | 1560.76 | 0.065864 | 2225.93 | 0.062526 | 2737.85 | 0.060983 | 3360.78 | 0.058067 | 3983.55 | 0.060195 | 4554.76 | 0.064431 | 500.212 | 5.3445 | 541.963 | 6.9719 | 591.249 | 7.9584 | 621.094 | 11.5359 | 671.78 | 27.4942 | 838.434 | 31.0092 | 1064.56 | 35.3766 | 1451.14 | 16.4743 | 2196.64 | 7.8228
701.297 | 0.079805 | 887.076 | 0.077602 | 1100.95 | 0.072428 | 1453.79 | 0.069102 | 2071.29 | 0.065798 | 2568.12 | 0.064109 | 3174.57 | 0.060678 | 3710.52 | 0.064238 | 4150.27 | 0.070923 | 454.073 | 7.154 | 512.094 | 8.6131 | 554.203 | 10.2811 | 589.558 | 15.3534 | 646.495 | 39.7168 | 812.44 | 41.9864 | 1034.51 | 46.3344 | 1398.12 | 20.6935 | 2081.53 | 9.5652
634.559 | 0.085506 | 807.49 | 0.082896 | 974.506 | 0.078853 | 1350.09 | 0.073009 | 1944.83 | 0.069102 | 2404.09 | 0.067666 | 3010.7 | 0.063535 | 3470.06 | 0.068278 | 3831.18 | 0.077292 | 415.27 | 9.6532 | 473.185 | 11.5822 | 527.27 | 13.1681 | 565.422 | 20.2478 | 629.328 | 54.6148 | 797.688 | 53.2248 | 1003.01 | 65.3411 | 1350.13 | 26.7484 | 1981.5 | 11.8439
573.026 | 0.092258 | 744.662 | 0.088287 | 854 | 0.087234 | 1267.66 | 0.076446 | 1815.16 | 0.073156 | 2241.56 | 0.071923 | 2807.16 | 0.067262 | 3235.47 | 0.073302 | 3582.9 | 0.083479 | 387.028 | 12.7378 | 441.762 | 16.296 | 504.815 | 16.7216 | 540.414 | 29.132 | 614.373 | 80.2617 | 781.413 | 71.6957 | 978.06 | 87.8657 | 1306.77 | 34.3776 | 1912.39 | 14.4322
509.755 | 0.10145 | 686.037 | 0.094594 | 761.988 | 0.096408 | 1170.2 | 0.08158 | 1689.06 | 0.077602 | 2100.49 | 0.076141 | 2638.4 | 0.071207 | 2971.82 | 0.079965 | 3314.06 | 0.091523 | 367.587 | 16.1843 | 422.465 | 21.161 | 485.537 | 21.751 | 523.659 | 41.0352 | 608.073 | 113.705 | 772.072 | 93.9571 | 958.653 | 117.547 | 1264.08 | 46.8415 | 1822.58 | 18.538
457.113 | 0.11235 | 637.74 | 0.10085 | 692.931 | 0.10538 | 1085.64 | 0.086972 | 1557.64 | 0.083479 | 1937.06 | 0.082318 | 2411.32 | 0.077602 | 2743.33 | 0.087496 | 3099.29 | 0.099742 | 346.335 | 22.9019 | 404.474 | 29.434 | 468.87 | 28.6848 | 512.094 | 55.4344 | 603.563 | 161.64 | 765.908 | 126.346 | 942.865 | 148.925 | 1239 | 58.3008 | 1752.98 | 23.3658
412.374 | 0.12454 | 586.358 | 0.10924 | 625.112 | 0.11717 | 983.316 | 0.095163 | 1433.58 | 0.09016 | 1786.35 | 0.089263 | 2219.26 | 0.084402 | 2547.65 | 0.095068 | 2878.22 | 0.10946 | 331.966 | 32.1488 | 394.185 | 37.8291 | 455.897 | 36.5928 | 502.508 | 78.0846 | 601.149 | 229.124 | 761.535 | 165.576 | 928.4 | 187.28 | 1213.72 | 79.075 | 1688.93 | 29.637
362.104 | 0.14354 | 535.891 | 0.11989 | 561.118 | 0.13197 | 892.415 | 0.10496 | 1316.76 | 0.098454 | 1662.25 | 0.096698 | 2075.44 | 0.090794 | 2326.05 | 0.10633 | 2565.55 | 0.12807 | 319.838 | 48.0097 | 384.157 | 50.9279 | 443.791 | 48.1199 | 495.933 | 112.732 | 600.805 | 327.962 | 762.844 | 230.573 | 912.588 | 253.141 | 1190.32 | 106.944 | 1642.2 | 36.9932
330.277 | 0.16023 | 496.673 | 0.13014 | 507.721 | 0.1488 | 793.879 | 0.1187 | 1209.46 | 0.10794 | 1559.2 | 0.10381 | 1898.71 | 0.10024 | 2121.6 | 0.11929 | 2363.57 | 0.14382 | 312.058 | 67.0092 | 376.966 | 66.7792 | 432.997 | 65.4911 | 492.537 | 158.431 | 601.149 | 431.026 | 763.718 | 317.789 | 897.558 | 338.848 | 1171.39 | 139.59 | 1612.38 | 43.6794
293.222 | 0.18672 | 456.656 | 0.14296 | 474.343 | 0.162 | 731.378 | 0.13079 | 1129.95 | 0.1167 | 1456.7 | 0.11224 | 1735.29 | 0.11156 | 1942.88 | 0.13477 | 2162.3 | 0.16395 | 306.919 | 97.6337 | 370.97 | 90.8344 | 426.11 | 89.0822 | 490.848 | 220.875 | 603.563 | 541.723 | 762.407 | 416.462 | 889.882 | 429.301 | 1152.09 | 189.764 | 1568.67 | 55.4662
253.898 | 0.22737 | 416.935 | 0.16023 | 440.95 | 0.1785 | 673.798 | 0.14512 | 1038.91 | 0.1291 | 1359.57 | 0.12183 | 1598.67 | 0.12342 | 1773.89 | 0.15287 | 1988.09 | 0.18616 | 303.077 | 133.184 | 368.008 | 119.311 | 421.016 | 115.942 | 490.006 | 303.205 | 605.294 | 602.291 | 761.971 | 506.602 | 881.261 | 522.52 | 1142.24 | 248.828 | 1534.9 | 68.484
221.613 | 0.27911 | 379.909 | 0.1812 | 400.187 | 0.20369 | 615.805 | 0.16249 | 967.708 | 0.14112 | 1256.3 | 0.13437 | 1466.93 | 0.13805 | 1627.71 | 0.17253 | 1826.08 | 0.21264 | 301.519 | 196.175 | 366.117 | 158.885 | 417.177 | 159.067 | 490.006 | 412.662 |  |  | 762.407 | 601.257 |  |  | 1130.53 | 336.527 | 1496.71 | 89.7481
199.923 | 0.32688 | 345.133 | 0.20574 | 363.919 | 0.23336 | 554.979 | 0.18709 | 901.384 | 0.15487 | 1162.03 | 0.14954 | 1384.27 | 0.14999 | 1504.07 | 0.19453 | 1716.3 | 0.235 | 300.657 | 281.928 | 365.07 | 210.739 | 414.083 | 207.386 | 490.286 | 531.578 | [6 empty] | 1120.86 | 420.779 | 1467.01 | 113.77
178.561 | 0.39409 | 316.06 | 0.23383 | 334.264 | 0.26549 | 506.706 | 0.21328 | 838.765 | 0.17065 | 1080.23 | 0.16511 | 1297.15 | 0.16412 | 1391.21 | 0.21868 | 1568.58 | 0.27221 | 300.485 | 418.615 | 362.778 | 283.386 | 412.426 | 278.238 | 490.286 | 600.913 | [6 empty] | 1115.1 | 513.91 | 1438.73 | 147.566
163.029 | 0.45879 | 290.886 | 0.26417 | 305.494 | 0.30539 | 450.308 | 0.25381 | 772.731 | 0.19125 | 1008.2 | 0.18284 | 1219.17 | 0.17993 | 1279.12 | 0.25053 | 1478.71 | 0.30054 | 300.829 | 534.326 | 362.57 | 360.683 | 410.541 | 373.296 | [8 empty] | 1111.91 | 526.124 | 1410.99 | 189.221
150.194 | 0.52826 | 266.382 | 0.30387 | 280.881 | 0.35058 | 406.235 | 0.29875 | 721.932 | 0.212 | 926.979 | 0.20656 | 1144.73 | 0.19747 | 1179.6 | 0.2856 | 1402.38 | 0.33049 | 302.037 | 601.946 | 362.57 | 487.525 | 409.837 | 486.688 | [10 empty] | 1390.14 | 239.458
139.76 | 0.6022 | 247.381 | 0.34124 | 258.509 | 0.40085 | 379.529 | 0.33448 | 668.43 | 0.23855 | 817.238 | 0.25053 | 1068.41 | 0.21933 | 1094.36 | 0.32298 | 1303.65 | 0.37563 |  |  | 363.193 | 580.941 | 410.776 | 588.309 | [10 empty] | 1367.24 | 313.45
121.259 | 0.77712 | 226.996 | 0.39252 | 238.873 | 0.45879 | 340.335 | 0.40045 | 623.24 | 0.26576 | 735.044 | 0.29755 | 984.3 | 0.24978 | 1021.4 | 0.36307 | 1217.95 | 0.42564 |  |  | 362.778 | 599.194 | 410.776 | 602.982 | [10 empty] | 1352.45 | 388.793
107.87 | 0.96642 | 207.666 | 0.45559 | 224.288 | 0.51316 | 309.182 | 0.47276 | 575.898 | 0.30114 | 668.43 | 0.34744 | 924.202 | 0.27661 | 952.348 | 0.40936 | 1129.95 | 0.4896 | [16 empty] | 1337.81 | 467.021
97.5079 | 1.171 | 189.224 | 0.53411 | 210.594 | 0.57112 | 288.28 | 0.53464 | 541.277 | 0.33382 | 605.425 | 0.411 | 860.859 | 0.31125 | 888.852 | 0.46155 | 1054.61 | 0.55646 | [16 empty] | 1331.7 | 524.619
89.2939 | 1.3991 | 165.825 | 0.68307 | 196.946 | 0.64072 | 270.408 | 0.5974 | 502.669 | 0.37751 | 549.457 | 0.48814 | 803.463 | 0.34953 | 824.627 | 0.5251 | 969.646 | 0.65301
81.3641 | 1.6834 | 148.403 | 0.8343 | 178.919 | 0.76402 | 254.915 | 0.66023 | 465.881 | 0.42992 | 500.662 | 0.57628 | 749.893 | 0.39409 | 765.808 | 0.60341 | 915.922 | 0.73406
75.1837 | 1.9874 | 134.684 | 1.0028 | 166.489 | 0.87358 | 236.496 | 0.75415 | 430.063 | 0.49502 | 460.324 | 0.6662 | 702.701 | 0.44168 | 723.377 | 0.66754 | 854.854 | 0.84353
70.2411 | 2.3068 | 122.233 | 1.2139 | 155.856 | 0.99386 | 222.278 | 0.84945 | 398.191 | 0.566 | 420.705 | 0.7818 | 640.296 | 0.52301 | 675.823 | 0.75415 | 803.463 | 0.95967
66.283 | 2.6454 | 110.822 | 1.4856 | 145.464 | 1.1409 | 206.217 | 0.97808 | 368.312 | 0.64781 | 387.583 | 0.90923 | 582.268 | 0.62428 | 622.617 | 0.88147 | 743.918 | 1.1296
62.423 | 3.043 | 99.9763 | 1.8531 | 134.146 | 1.3469 | 194.402 | 1.0973 | 325.685 | 0.8137 | 362.104 | 1.0334 | 532.153 | 0.74292 | 583.434 | 0.99386 | 698.497 | 1.2851
59.1416 | 3.4759 | 93.4974 | 2.1401 | 124.827 | 1.5634 | 183.081 | 1.2347 | 297.654 | 0.9616 | 337.961 | 1.1816 | 497.667 | 0.84776 | 551.108 | 1.1105 | 649.973 | 1.4916
55.6974 | 4.0222 | 87.3509 | 2.5014 | 114.77 | 1.8811 | 173.804 | 1.3741 | 272.307 | 1.1432 | 314.483 | 1.3618 | 468.217 | 0.95584 | 516.426 | 1.2584 | 610.288 | 1.7055
52.1401 | 4.8059 | 82.1818 | 2.883 | 108.519 | 2.1251 | 164.175 | 1.5432 | 252.379 | 1.3269 | 292.929 | 1.5759 | 437.874 | 1.1006 | 491.239 | 1.3907 | 577.629 | 1.921
49.1528 | 5.6908 | 77.2413 | 3.3462 | 103.124 | 2.3651 | 155.544 | 1.7312 | 235.316 | 1.5309 | 276.146 | 1.7822 | 414.856 | 1.2322 | 468.685 | 1.5324 | 551.66 | 2.1401
46.383 | 6.6782 | 73.7687 | 3.7691 | 98.3895 | 2.6139 | 147.958 | 1.9287 | 222.723 | 1.7226 | 257.735 | 2.0665 | 395.018 | 1.3646 | 444.492 | 1.7209 | 527.385 | 2.3604
44.1651 | 7.7589 | 69.6814 | 4.3967 | 93.3106 | 2.9649 | 139.76 | 2.1921 | 209.334 | 1.9676 | 242.968 | 2.3675 | 372.759 | 1.5509 | 420.284 | 1.952 | 498.165 | 2.7043
42.2217 | 8.8804 | 66.0845 | 5.0776 | 89.2939 | 3.3196 | 132.414 | 2.4889 | 196.749 | 2.2453 | 229.736 | 2.6935 | 355.289 | 1.7278 | 399.387 | 2.2008 | 471.034 | 3.0828
40.6474 | 10.2148 | 62.548 | 5.9527 | 85.1091 | 3.7578 | 126.714 | 2.77 | 183.081 | 2.6561 | 219.627 | 3.0127 | 335.268 | 1.9696 | 381.813 | 2.4518 | 446.273 | 3.4933
39.3279 | 11.7852 | 59.557 | 6.9855 | 81.8537 | 4.1906 | 120.413 | 3.1451 | 174.327 | 2.9738 | 207.666 | 3.4759 | 322.445 | 2.1551 | 362.829 | 2.7727 | 425.784 | 3.9505
37.8236 | 14.3801 | 56.9364 | 8.1976 | 78.4086 | 4.7107 | 114.77 | 3.5603 | 164.339 | 3.4241 | 197.933 | 3.9269 | 310.111 | 2.3628 | 344.1 | 3.1831 | 409.088 | 4.3879
36.6691 | 17.6519 | 54.5945 | 9.6104 | 75.5605 | 5.2954 | 110.049 | 3.9783 | 155.078 | 3.9743 | 189.792 | 4.4187 | 300.345 | 2.5698 | 328.63 | 3.6069 | 393.441 | 4.9079
35.6566 | 21.8204 | 52.6115 | 11.2666 | 73.3274 | 5.9053 | 105.207 | 4.5215 | 148.998 | 4.4453 | 183.265 | 4.903 | 287.416 | 2.8486 | 313.228 | 4.1158 | 378.014 | 5.5005
35.0205 | 25.9935 | 50.9036 | 13.3277 | 70.5932 | 6.8609 | 101.183 | 5.0725 | 144.161 | 4.8688 | 178.204 | 5.3433 | 278.643 | 3.0952 | 299.146 | 4.7438 | 363.919 | 6.1217
34.3271 | 32.6174 | 49.6468 | 15.5311 | 68.1652 | 7.9315 | 97.4105 | 5.6908 | 138.647 | 5.397 | 171.56 | 6.0005 | 268.253 | 3.4207 | 287.992 | 5.3113 | 351.754 | 6.7723
33.816 | 39.3245 | 48.3726 | 18.6127 | 65.6892 | 9.3357 | 94.0601 | 6.4099 | 133.477 | 5.9885 | 165.99 | 6.6982 | 258.251 | 3.7956 | 278.364 | 5.9586 | 337.961 | 7.6511
33.4461 | 48.4168 | 47.5572 | 21.6682 | 63.5568 | 10.9227 | 91.0068 | 7.1839 | 128.243 | 6.7927 | 161.73 | 7.4175 | 249.868 | 4.1697 | 267.717 | 6.7995 | 328.63 | 8.4981
33.2128 | 60.0903 | 46.99 | 25.301 | 62.0496 | 12.464 | 88.3171 | 8.0837 | 123.585 | 7.7434 | 156.95 | 8.3716 | 240.791 | 4.6685 | 259.545 | 7.7048 | 319.875 | 9.4673
33.0802 | 79.0317 | 46.3367 | 29.6911 | 60.5781 | 14.4666 | 85.8785 | 9.1692 | 119.813 | 8.722 | 151.856 | 9.4673 | 233.208 | 5.1492 | 251.371 | 8.9428 | 313.541 | 10.3485
33.0141 | 108.294 | 45.8298 | 34.7384 | 59.438 | 16.8078 | 83.9259 | 10.39 | 115.808 | 10.2148 | 147.81 | 10.8356 | 226.316 | 5.6851 | 244.186 | 10.2046 | 304.884 | 11.8206
33.0141 | 153.216 | 45.3284 | 40.9293 | 58.5531 | 19.4111 | 81.6085 | 12.0835 | 112.273 | 11.8561 | 143.873 | 12.4266 | 219.847 | 6.2454 | 239.351 | 11.4712 | 298.847 | 13.1687
33.0141 | 221.152 | 44.9223 | 48.5138 | 57.6814 | 23.2626 | 79.6732 | 14.011 | 109.173 | 13.6924 | 140.602 | 14.237 | 212.285 | 7.1195 | 233.675 | 12.9597 | 292.052 | 14.7884
33.0141 | 317.619 | 44.5643 | 58.6653 | 56.9364 | 27.6561 | 77.9396 | 16.0522 | 106.477 | 16.0201 | 136.993 | 16.7407 | 204.779 | 8.0998 | 229.736 | 14.4956 | 285.411 | 16.8752
32.9811 | 467.712 | 44.3864 | 72.519 | 56.3135 | 33.4097 | 76.856 | 18.1169 | 104.578 | 18.3173 | 134.012 | 19.4111 | 198.528 | 9.2243 | 225.638 | 16.2297 | 279.76 | 19.0648
32.9481 | 545.582 | 44.1651 | 91.6383 | 55.7532 | 40.0788 | 75.4095 | 21.3456 | 102.507 | 21.4311 | 130.312 | 23.5434 | 192.276 | 10.6211 | 221.834 | 18.1895 | 273.399 | 22.0397
32.9152 | 599.954 | 44.1651 | 121.613 | 55.3642 | 49.3456 | 74.1384 | 24.8248 | 100.477 | 25.1245 | 127.987 | 27.8782 | 187.154 | 12.1198 | 216.574 | 21.3669 | 266.648 | 26.0716
|  | 44.1651 | 157.095 | 55.1984 | 62.4801 | 73.1809 | 29.074 | 98.5864 | 29.1906 | 125.578 | 33.0112 | 182.168 | 14.3657 | 213.136 | 24.8 | 262.154 | 29.7208
|  | 44.1651 | 198.314 | 55.1984 | 81.9287 | 72.0913 | 34.3928 | 97.4105 | 33.6444 | 123.709 | 38.7778 | 178.383 | 16.6239 | 209.334 | 29.5134 | 257.735 | 34.7384
|  | 44.1651 | 274.198 | 55.1984 | 111.146 | 71.1602 | 41.382 | 95.8643 | 39.8789 | 122.111 | 45.6885 | 174.501 | 19.2757 | 204.984 | 36.1923 | 253.644 | 39.3245
|  | 44.1651 | 357.041 | 55.1984 | 144.005 | 70.3817 | 50.3424 | 94.6261 | 46.7983 | 120.413 | 55.5258 | 170.193 | 23.2858 | 201.126 | 44.073 | 249.868 | 45.4152
|  | 44.0768 | 437.402 | 55.1984 | 187.889 | 69.5422 | 61.3655 | 93.404 | 56.0839 | 119.096 | 65.7493 | 167.491 | 27.7392 | 197.736 | 54.0467 | 246.148 | 54.4808
|  | 44.0328 | 541.776 | 55.1984 | 253.623 | 68.9881 | 73.9101 | 92.6597 | 65.9468 | 117.558 | 81.8468 | 164.668 | 33.2431 | 195.182 | 63.4878 | 242.968 | 63.6149
|  | 43.9888 | 599.954 | 55.1984 | 345.451 | 68.3016 | 90.9081 | 91.8295 | 77.312 | 116.155 | 103.218 | 162.379 | 39.9987 | 192.853 | 74.2805 | 239.59 | 76.3898
|  |  |  | 55.1984 | 466.777 | 67.8252 | 113.618 | 91.0978 | 92.0056 | 115.115 | 126.83 | 160.442 | 47.08 | 190.744 | 87.169 | 236.26 | 91.6383
|  |  |  | 55.1984 | 566.713 | 67.4195 | 140.59 | 90.5529 | 108.728 | 113.514 | 168.149 | 158.528 | 56.365 | 188.28 | 102.601 | 229.736 | 135.89
|  |  |  | 55.1432 | 599.954 | 67.0162 | 180.161 | 90.1012 | 131.611 | 112.723 | 205.172 | 156.48 | 67.7516 | 186.78 | 118.019 | 227.223 | 161.717
[6 empty] | 66.7486 | 228.572 | 89.7415 | 152.91 | 112.16 | 254.895 | 154.768 | 80.3867 | 185.106 | 136.982 | 222.278 | 237.425
[6 empty] | 66.4822 | 295.258 | 88.8486 | 188.077 | 111.601 | 314.458 | 152.312 | 103.012 | 183.631 | 161.233 | 220.507 | 280.858
[6 empty] | 66.283 | 365.714 | 88.5824 | 239.332 | 111.155 | 384.849 | 148.254 | 168.991 | 181.804 | 191.684 | 218.75 | 330.581
[6 empty] | 66.2168 | 452.077 | 88.1406 | 309.777 | 110.49 | 487.287 | 146.779 | 205.789 | 178.919 | 269.307 | 217.007 | 414.408
[6 empty] | 66.0845 | 540.153 | 88.0525 | 599.954 | 110.27 | 570.124 | 144.45 | 324.359 | 176.961 | 372.357 | 215.925 | 497.131
[6 empty] | 66.0845 | 599.954 |  |  | 110.049 | 599.954 | 142.584 | 599.954 | 173.978 | 599.954 | 215.278 | 599.954