## Min. Melt
S&C Fault Fiter Electronic Power Fuses | [9 empty] | S&C Fault Fiter Electronic Power Fuses | [9 empty] | S&C Fault Fiter Electronic Power Fuses | [9 empty] | S&C Fault Fiter Electronic Power Fuses | [9 empty] | S&C Fault Fiter Electronic Power Fuses | [9 empty] | S&C Fault Fiter Electronic Power Fuses | [9 empty] | S&C Fault Fiter Electronic Power Fuses
Time-Delayed Compound-Curve-Type Control Modules (TCC 421-7) | [9 empty] | Time-Delayed Compound-Curve-Type Control Modules (TCC 421-7) | [9 empty] | Time-Delayed Compound-Curve-Type Control Modules (TCC 421-7) | [9 empty] | Time-Delayed Compound-Curve-Type Control Modules (TCC 421-7) | [9 empty] | Time-Delayed Compound-Curve-Type Control Modules (TCC 421-7) | [9 empty] | Time-Delayed Compound-Curve-Type Control Modules (TCC 421-7) | [9 empty] | Time-Delayed Compound-Curve-Type Control Modules (TCC 421-7)
Minimum Melting Time-Current Characteristic Curve Dated January 9, 1989 | [9 empty] | Minimum Melting Time-Current Characteristic Curve Dated January 9, 1989 | [9 empty] | Total Clearing Time-Current Characteristic Curve Dated January 9, 1989 | [9 empty] | Total Clearing Time-Current Characteristic Curve Dated January 9, 1989 | [9 empty] | Total Clearing Time-Current Characteristic Curve Dated January 9, 1989 | [9 empty] | Total Clearing Time-Current Characteristic Curve Dated January 9, 1989 | [9 empty] | Total Clearing Time-Current Characteristic Curve Dated January 9, 1989
Tolerance in Terms of Current: Plus 10% | [9 empty] | Tolerance in Terms of Current: Plus 10% | [9 empty] | Tolerance in Terms of Current: Plus 10% | [9 empty] | Tolerance in Terms of Current: Plus 10% | [9 empty] | Tolerance in Terms of Current: Plus 10% | [9 empty] | Tolerance in Terms of Current: Plus 10% | [9 empty] | Tolerance in Terms of Current: Plus 10%
7010-C40S1T3D8 |  | 7010-C40S1T6D8 |  | 7010-C40S2T3D8 |  | 7010-C40S2T6D8 |  | 7010-C40S3T3D8 |  | 7010-C40S3T6D8 |  | 7010-C40S4T3D8 |  | 7010-C40S4T6D8 |  | 7010-C60S1T3D8 |  | 7010-C60S1T6D8 |  | 7010-C60S2T3D8 |  | 7010-C60S2T6D8 |  | 7010-C60S3T3D8 |  | 7010-C60S3T6D8 |  | 7010-C60S4T3D8 |  | 7010-C60S4T6D8 |  | 7010-C80S1T3D8 |  | 7010-C80S1T6D8 |  | 7010-C80S2T3D8 |  | 7010-C80S2T6D8 |  | 7010-C80S3T3D8 |  | 7010-C80S3T6D8 |  | 7010-C80S4T3D8 |  | 7010-C80S4T6D8 |  | 7010-C110S1T3D8 |  | 7010-C110S1T6D8 |  | 7010-C110S2T3D8 |  | 7010-C110S2T6D8 |  | 7010-C110S3T3D8 |  | 7010-C110S3T6D8 |  | 7010-C110S4T3D8 |  | 7010-C110S4T6D8
Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time
3750.16 | 0.01 | 6395.51 | 0.01 | 3750.16 | 0.01 | 6395.51 | 0.01 | 3750.16 | 0.01 | 6395.51 | 0.01 | 3750.16 | 0.01 | 6395.51 | 0.01 | 3750.16 | 0.01 | 6395.51 | 0.01 | 3750.16 | 0.01 | 6395.51 | 0.01 | 3750.16 | 0.01 | 6395.51 | 0.01 | 3750.16 | 0.01 | 6395.51 | 0.01 | 3750.16 | 0.01 | 6395.51 | 0.01 | 3750.16 | 0.01 | 6395.51 | 0.01 | 3750.16 | 0.01 | 6395.51 | 0.01 | 3750.16 | 0.01 | 6395.51 | 0.01 | 3750.16 | 0.01 | 6395.51 | 0.01 | 3750.16 | 0.01 | 6395.51 | 0.01 | 3750.16 | 0.01 | 6395.51 | 0.01 | 3750.16 | 0.01 | 6395.51 | 0.01
3750.16 | 0.01 | 6395.51 | 0.01 | 3750.16 | 0.01 | 6395.51 | 0.01 | 3750.16 | 0.01 | 6395.51 | 0.01 | 3750.16 | 0.01 | 6395.51 | 0.01 | 3750.16 | 0.01 | 6395.51 | 0.01 | 3750.16 | 0.01 | 6395.51 | 0.01 | 3750.16 | 0.01 | 6395.51 | 0.01 | 3750.16 | 0.01 | 6395.51 | 0.01 | 3750.16 | 0.01 | 6395.51 | 0.01 | 3750.16 | 0.01 | 6395.51 | 0.01 | 3750.16 | 0.01 | 6395.51 | 0.01 | 3750.16 | 0.01 | 6395.51 | 0.01 | 3750.16 | 0.01 | 6395.51 | 0.01 | 3750.16 | 0.01 | 6395.51 | 0.01 | 3750.16 | 0.01 | 6395.51 | 0.01 | 3750.16 | 0.01 | 6395.51 | 0.01
3750.16 | 0.018882 | 6395.51 | 0.017604 | 3750.16 | 0.018882 | 6395.51 | 0.017604 | 3750.16 | 0.018882 | 6395.51 | 0.017604 | 3750.16 | 0.018882 | 6395.51 | 0.017604 | 3750.16 | 0.018882 | 6395.51 | 0.017604 | 3750.16 | 0.018882 | 6395.51 | 0.017604 | 3750.16 | 0.018882 | 6395.51 | 0.017604 | 3750.16 | 0.018882 | 6395.51 | 0.017604 | 3750.16 | 0.018882 | 6395.51 | 0.017604 | 3750.16 | 0.018882 | 6395.51 | 0.017604 | 3750.16 | 0.018882 | 6395.51 | 0.017604 | 3750.16 | 0.018882 | 6395.51 | 0.017604 | 3750.16 | 0.018882 | 6395.51 | 0.017604 | 3750.16 | 0.018882 | 6395.51 | 0.017604 | 3750.16 | 0.018882 | 6395.51 | 0.017604 | 3750.16 | 0.018882 | 6395.51 | 0.017604
2972.61 | 0.020209 | 5918.86 | 0.020486 | 2972.61 | 0.020209 | 5918.86 | 0.020486 | 2972.61 | 0.020209 | 5918.86 | 0.020486 | 2972.61 | 0.020209 | 5918.86 | 0.020486 | 2972.61 | 0.020209 | 5918.86 | 0.020486 | 2972.61 | 0.020209 | 5918.86 | 0.020486 | 2972.61 | 0.020209 | 5918.86 | 0.020486 | 2972.61 | 0.020209 | 5918.86 | 0.020486 | 2972.61 | 0.020209 | 5918.86 | 0.020486 | 2972.61 | 0.020209 | 5918.86 | 0.020486 | 2972.61 | 0.020209 | 5918.86 | 0.020486 | 2972.61 | 0.020209 | 5918.86 | 0.020486 | 2972.61 | 0.020209 | 5918.86 | 0.020486 | 2972.61 | 0.020209 | 5918.86 | 0.020486 | 2972.61 | 0.020209 | 5918.86 | 0.020486 | 2972.61 | 0.020209 | 5918.86 | 0.020486
2938.58 | 0.14067 | 5918.86 | 0.057847 | 2938.58 | 0.14067 | 5918.86 | 0.057847 | 2938.58 | 0.14067 | 5918.86 | 0.057847 | 2938.58 | 0.14067 | 5918.86 | 0.057847 | 2938.58 | 0.14067 | 5918.86 | 0.057847 | 2938.58 | 0.14067 | 5918.86 | 0.057847 | 2938.58 | 0.14067 | 5918.86 | 0.057847 | 2938.58 | 0.14067 | 5918.86 | 0.057847 | 2938.58 | 0.14067 | 5918.86 | 0.057847 | 2938.58 | 0.14067 | 5918.86 | 0.057847 | 2938.58 | 0.14067 | 5918.86 | 0.057847 | 2938.58 | 0.14067 | 5918.86 | 0.057847 | 2938.58 | 0.14067 | 5918.86 | 0.057847 | 2938.58 | 0.14067 | 5918.86 | 0.057847 | 2938.58 | 0.14067 | 5918.86 | 0.057847 | 2938.58 | 0.14067 | 5918.86 | 0.057847
2938.58 | 0.14067 | 5918.86 | 0.08481 | 2938.58 | 0.26588 | 5918.86 | 0.08481 | 2938.58 | 0.51209 | 5918.86 | 0.08481 | 2938.58 | 0.99043 | 5918.86 | 0.08481 | 2938.58 | 0.14067 | 5918.86 | 0.08481 | 2938.58 | 0.26588 | 5918.86 | 0.08481 | 2938.58 | 0.51209 | 5918.86 | 0.08481 | 2938.58 | 0.99043 | 5918.86 | 0.08481 | 2938.58 | 0.14067 | 5918.86 | 0.08481 | 2938.58 | 0.26588 | 5918.86 | 0.08481 | 2938.58 | 0.51209 | 5918.86 | 0.08481 | 2938.58 | 0.99043 | 5918.86 | 0.08481 | 2938.58 | 0.14067 | 5918.86 | 0.08481 | 2938.58 | 0.26588 | 5918.86 | 0.08481 | 2938.58 | 0.51209 | 5918.86 | 0.08481 | 2938.58 | 0.99043 | 5918.86 | 0.08481
1917.25 | 0.21436 | 4116.29 | 0.10798 | 2236.14 | 0.3471 | 5918.86 | 0.14915 | 2403.6 | 0.62526 | 5918.86 | 0.27781 | 2411.16 | 1.2169 | 5918.86 | 0.53675 | 1917.25 | 0.21436 | 4116.29 | 0.10798 | 2236.14 | 0.3471 | 5918.86 | 0.14915 | 2403.6 | 0.62526 | 5918.86 | 0.27781 | 2411.16 | 1.2169 | 5918.86 | 0.53675 | 1917.25 | 0.21436 | 4116.29 | 0.10798 | 2236.14 | 0.3471 | 5918.86 | 0.14915 | 2403.6 | 0.62526 | 5918.86 | 0.27781 | 2411.16 | 1.2169 | 5918.86 | 0.53675 | 1917.25 | 0.21436 | 4116.29 | 0.10798 | 2236.14 | 0.3471 | 5918.86 | 0.14915 | 2403.6 | 0.62526 | 5918.86 | 0.27781 | 2411.16 | 1.2169 | 5918.86 | 0.53675
1237.86 | 0.34782 | 2938.58 | 0.14067 | 1469.67 | 0.5441 | 4150.9 | 0.19573 | 1652.46 | 0.93803 | 4378.5 | 0.35332 | 1726.72 | 1.7472 | 4190.19 | 0.71329 | 1237.86 | 0.34782 | 2938.58 | 0.14067 | 1469.67 | 0.5441 | 4150.9 | 0.19573 | 1652.46 | 0.93803 | 4378.5 | 0.35332 | 1726.72 | 1.7472 | 4190.19 | 0.71329 | 1237.86 | 0.34782 | 2938.58 | 0.14067 | 1469.67 | 0.5441 | 4150.9 | 0.19573 | 1652.46 | 0.93803 | 4378.5 | 0.35332 | 1726.72 | 1.7472 | 4190.19 | 0.71329 | 1237.86 | 0.34782 | 2938.58 | 0.14067 | 1469.67 | 0.5441 | 4150.9 | 0.19573 | 1652.46 | 0.93803 | 4378.5 | 0.35332 | 1726.72 | 1.7472 | 4190.19 | 0.71329
1091.75 | 0.4073 | 2938.58 | 0.14067 | 1091.75 | 0.77227 | 2938.58 | 0.26588 | 1276.01 | 1.2649 | 2938.58 | 0.51209 | 1091.75 | 3.0248 | 2938.58 | 0.99043 | 1091.75 | 0.4073 | 2938.58 | 0.14067 | 1091.75 | 0.77227 | 2938.58 | 0.26588 | 1276.01 | 1.2649 | 2938.58 | 0.51209 | 1091.75 | 3.0248 | 2938.58 | 0.99043 | 1091.75 | 0.4073 | 2938.58 | 0.14067 | 1091.75 | 0.77227 | 2938.58 | 0.26588 | 1276.01 | 1.2649 | 2938.58 | 0.51209 | 1091.75 | 3.0248 | 2938.58 | 0.99043 | 1091.75 | 0.4073 | 2938.58 | 0.14067 | 1091.75 | 0.77227 | 2938.58 | 0.26588 | 1276.01 | 1.2649 | 2938.58 | 0.51209 | 1091.75 | 3.0248 | 2938.58 | 0.99043
794.22 | 0.60028 | 1917.25 | 0.21436 | 794.22 | 1.1429 | 2236.14 | 0.3471 | 1091.75 | 1.5348 | 2403.6 | 0.62526 | 868.117 | 4.0492 | 2411.16 | 1.2169 | 794.22 | 0.60028 | 1917.25 | 0.21436 | 794.22 | 1.1429 | 2236.14 | 0.3471 | 1091.75 | 1.5348 | 2403.6 | 0.62526 | 868.117 | 4.0492 | 2411.16 | 1.2169 | 794.22 | 0.60028 | 1917.25 | 0.21436 | 794.22 | 1.1429 | 2236.14 | 0.3471 | 1091.75 | 1.5348 | 2403.6 | 0.62526 | 868.117 | 4.0492 | 2411.16 | 1.2169 | 1091.75 | 4.7815 | 1917.25 | 0.21436 | 1091.75 | 4.7815 | 2236.14 | 0.3471 | 1091.75 | 1.5348 | 2403.6 | 0.62526 | 1091.75 | 4.7815 | 2411.16 | 1.2169
592.467 | 0.89212 | 1237.86 | 0.34782 | 592.467 | 1.6774 | 1469.67 | 0.5441 | 794.22 | 2.2738 | 1652.46 | 0.93803 | 794.22 | 4.538 | 1726.72 | 1.7472 | 592.467 | 0.89212 | 1237.86 | 0.34782 | 592.467 | 1.6774 | 1469.67 | 0.5441 | 794.22 | 2.2738 | 1652.46 | 0.93803 | 794.22 | 4.538 | 1726.72 | 1.7472 | 794.22 | 6.0811 | 1237.86 | 0.34782 | 794.22 | 6.0811 | 1469.67 | 0.5441 | 794.22 | 2.2738 | 1652.46 | 0.93803 | 794.22 | 4.538 | 1726.72 | 1.7472 | 1091.75 | 65.5237 | 1237.86 | 0.34782 | 1091.75 | 65.5237 | 1469.67 | 0.5441 | 1091.75 | 4.7815 | 1652.46 | 0.93803 | 1091.75 | 65.5237 | 1726.72 | 1.7472
396.382 | 1.8086 | 1091.75 | 0.4073 | 472.09 | 2.3709 | 1091.75 | 0.77227 | 592.467 | 3.3477 | 1276.01 | 1.2649 | 684.531 | 5.5408 | 1091.75 | 3.0248 | 592.467 | 8.8044 | 1091.75 | 0.4073 | 592.467 | 8.8044 | 1091.75 | 0.77227 | 592.467 | 3.3477 | 1276.01 | 1.2649 | 684.531 | 5.5408 | 1091.75 | 3.0248 | 794.22 | 68.5363 | 1091.75 | 0.4073 | 794.22 | 68.5363 | 1091.75 | 0.77227 | 794.22 | 6.0811 | 1276.01 | 1.2649 | 794.22 | 6.0811 | 1091.75 | 3.0248 | 1091.75 | 1000 | 1091.75 | 0.4073 | 1091.75 | 1000 | 1091.75 | 0.77227 | 1091.75 | 65.5237 | 1276.01 | 1.2649 | 1091.75 | 1000 | 1091.75 | 3.0248
396.382 | 11.8231 | 794.22 | 0.60028 | 396.382 | 3.2375 | 794.22 | 1.1429 | 396.382 | 5.7054 | 1091.75 | 1.5348 | 592.467 | 6.695 | 868.117 | 4.0492 | 592.467 | 104.444 | 794.22 | 0.60028 | 592.467 | 104.444 | 794.22 | 1.1429 | 592.467 | 8.8044 | 1091.75 | 1.5348 | 592.467 | 6.695 | 868.117 | 4.0492 | 794.22 | 1000 | 794.22 | 0.60028 | 794.22 | 1000 | 794.22 | 1.1429 | 794.22 | 68.5363 | 1091.75 | 1.5348 | 794.22 | 68.5363 | 868.117 | 4.0492 |  |  | 1091.75 | 4.7815 |  |  | 1091.75 | 4.7815 | 1091.75 | 1000 | 1091.75 | 1.5348 |  |  | 1091.75 | 4.7815
396.382 | 313.364 | 592.467 | 0.89212 | 396.382 | 11.8231 | 592.467 | 1.6774 | 396.382 | 11.8231 | 794.22 | 2.2738 | 506.915 | 8.2951 | 794.22 | 4.538 | 592.467 | 1000 | 592.467 | 0.89212 | 592.467 | 1000 | 592.467 | 1.6774 | 592.467 | 104.444 | 794.22 | 2.2738 | 592.467 | 8.8044 | 794.22 | 4.538 |  |  | 794.22 | 6.0811 |  |  | 794.22 | 6.0811 | 794.22 | 1000 | 794.22 | 2.2738 | 794.22 | 1000 | 794.22 | 4.538 |  |  | 1091.75 | 65.5237 |  |  | 1091.75 | 65.5237 |  |  | 1091.75 | 4.7815 |  |  | 1091.75 | 65.5237
396.382 | 1000 | 396.382 | 1.8086 | 396.382 | 313.364 | 472.09 | 2.3709 | 396.382 | 313.364 | 592.467 | 3.3477 | 396.382 | 11.5906 | 684.531 | 5.5408 |  |  | 592.467 | 8.8044 |  |  | 592.467 | 8.8044 | 592.467 | 1000 | 592.467 | 3.3477 | 592.467 | 104.444 | 684.531 | 5.5408 |  |  | 794.22 | 68.5363 |  |  | 794.22 | 68.5363 |  |  | 794.22 | 6.0811 |  |  | 794.22 | 6.0811 |  |  | 1091.75 | 1000 |  |  | 1091.75 | 1000 |  |  | 1091.75 | 65.5237 |  |  | 1091.75 | 1000
|  | 396.382 | 11.8231 | 396.382 | 1000 | 396.382 | 3.2375 | 396.382 | 1000 | 396.382 | 5.7054 | 396.382 | 11.8231 | 592.467 | 6.695 |  |  | 592.467 | 104.444 |  |  | 592.467 | 104.444 |  |  | 592.467 | 8.8044 | 592.467 | 1000 | 592.467 | 6.695 |  |  | 794.22 | 1000 |  |  | 794.22 | 1000 |  |  | 794.22 | 68.5363 |  |  | 794.22 | 68.5363 | [10 empty] | 1091.75 | 1000
|  | 396.382 | 313.364 |  |  | 396.382 | 11.8231 |  |  | 396.382 | 11.8231 | 396.382 | 313.364 | 506.915 | 8.2951 |  |  | 592.467 | 1000 |  |  | 592.467 | 1000 |  |  | 592.467 | 104.444 |  |  | 592.467 | 8.8044 | [10 empty] | 794.22 | 1000 |  |  | 794.22 | 1000
|  | 396.382 | 1000 |  |  | 396.382 | 313.364 |  |  | 396.382 | 313.364 | 396.382 | 1000 | 396.382 | 11.5906 | [10 empty] | 592.467 | 1000 |  |  | 592.467 | 104.444
[6 empty] | 396.382 | 1000 |  |  | 396.382 | 1000 |  |  | 396.382 | 11.8231 | [14 empty] | 592.467 | 1000
[14 empty] | 396.382 | 313.364
[14 empty] | 396.382 | 1000

## Total Clear
S&C Fault Fiter Electronic Power Fuses | [9 empty] | S&C Fault Fiter Electronic Power Fuses | [9 empty] | S&C Fault Fiter Electronic Power Fuses | [9 empty] | S&C Fault Fiter Electronic Power Fuses | [9 empty] | S&C Fault Fiter Electronic Power Fuses | [9 empty] | S&C Fault Fiter Electronic Power Fuses
Time-Delayed Compound-Curve-Type Control Modules (TCC 421-7) | [9 empty] | Time-Delayed Compound-Curve-Type Control Modules (TCC 421-7) | [9 empty] | Time-Delayed Compound-Curve-Type Control Modules (TCC 421-7) | [9 empty] | Time-Delayed Compound-Curve-Type Control Modules (TCC 421-7) | [9 empty] | Time-Delayed Compound-Curve-Type Control Modules (TCC 421-7) | [9 empty] | Time-Delayed Compound-Curve-Type Control Modules (TCC 421-7)
Total Clearing Time-Current Characteristic Curve Dated January 9, 1989 | [9 empty] | Total Clearing Time-Current Characteristic Curve Dated January 9, 1989 | [9 empty] | Total Clearing Time-Current Characteristic Curve Dated January 9, 1989 | [9 empty] | Total Clearing Time-Current Characteristic Curve Dated January 9, 1989 | [9 empty] | Total Clearing Time-Current Characteristic Curve Dated January 9, 1989 | [9 empty] | Total Clearing Time-Current Characteristic Curve Dated January 9, 1989
Tolerance in Terms of Current: Curves are plotted to maximum test points, all variations are minus. | [9 empty] | Tolerance in Terms of Current: Curves are plotted to maximum test points, all variations are minus. | [9 empty] | Tolerance in Terms of Current: Curves are plotted to maximum test points, all variations are minus. | [9 empty] | Tolerance in Terms of Current: Curves are plotted to maximum test points, all variations are minus. | [9 empty] | Tolerance in Terms of Current: Curves are plotted to maximum test points, all variations are minus. | [9 empty] | Tolerance in Terms of Current: Curves are plotted to maximum test points, all variations are minus.
7010-C40S3T6D8 |  | 7010-C40S4T3D8 |  | 7010-C40S4T6D8 |  | 7010-C60S1T3D8 |  | 7010-C60S1T6D8 |  | 7010-C60S2T3D8 |  | 7010-C60S2T6D8 |  | 7010-C60S3T3D8 |  | 7010-C60S3T6D8 |  | 7010-C60S4T3D8 |  | 7010-C60S4T6D8 |  | 7010-C80S1T3D8 |  | 7010-C80S1T6D8 |  | 7010-C80S2T3D8 |  | 7010-C80S2T6D8 |  | 7010-C80S3T3D8 |  | 7010-C80S3T6D8 |  | 7010-C80S4T3D8 |  | 7010-C80S4T6D8 |  | 7010-C110S1T3D8 |  | 7010-C110S1T6D8 |  | 7010-C110S2T3D8 |  | 7010-C110S2T6D8 |  | 7010-C110S3T3D8 |  | 7010-C110S3T6D8 |  | 7010-C110S4T3D8 |  | 7010-C110S4T6D8
Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time
40000 | 0.01 | 40000 | 0.01 | 40000 | 0.01 | 40000 | 0.01 | 40000 | 0.01 | 40000 | 0.01 | 40000 | 0.01 | 40000 | 0.01 | 40000 | 0.01 | 40000 | 0.01 | 40000 | 0.01 | 40000 | 0.01 | 40000 | 0.01 | 40000 | 0.01 | 40000 | 0.01 | 40000 | 0.01 | 40000 | 0.01 | 40000 | 0.01 | 40000 | 0.01 | 40000 | 0.01 | 40000 | 0.01 | 40000 | 0.01 | 40000 | 0.01 | 40000 | 0.01 | 40000 | 0.01 | 40000 | 0.01 | 40000 | 0.01
40000 | 0.021213 | 40000 | 0.021213 | 40000 | 0.021213 | 40000 | 0.021213 | 40000 | 0.021213 | 40000 | 0.021213 | 40000 | 0.021213 | 40000 | 0.021213 | 40000 | 0.021213 | 40000 | 0.021213 | 40000 | 0.021213 | 40000 | 0.021213 | 40000 | 0.021213 | 40000 | 0.021213 | 40000 | 0.021213 | 40000 | 0.021213 | 40000 | 0.021213 | 40000 | 0.021213 | 40000 | 0.021213 | 40000 | 0.021213 | 40000 | 0.021213 | 40000 | 0.021213 | 40000 | 0.021213 | 40000 | 0.021213 | 40000 | 0.021213 | 40000 | 0.021213 | 40000 | 0.021213
40000 | 0.021213 | 40000 | 0.021213 | 40000 | 0.021213 | 40000 | 0.021213 | 40000 | 0.021213 | 40000 | 0.021213 | 40000 | 0.021213 | 40000 | 0.021213 | 40000 | 0.021213 | 40000 | 0.021213 | 40000 | 0.021213 | 40000 | 0.021213 | 40000 | 0.021213 | 40000 | 0.021213 | 40000 | 0.021213 | 40000 | 0.021213 | 40000 | 0.021213 | 40000 | 0.021213 | 40000 | 0.021213 | 40000 | 0.021213 | 40000 | 0.021213 | 40000 | 0.021213 | 40000 | 0.021213 | 40000 | 0.021213 | 40000 | 0.021213 | 40000 | 0.021213 | 40000 | 0.021213
16114.8 | 0.021213 | 16114.8 | 0.021213 | 16114.8 | 0.021213 | 16114.8 | 0.021213 | 16114.8 | 0.021213 | 16114.8 | 0.021213 | 16114.8 | 0.021213 | 16114.8 | 0.021213 | 16114.8 | 0.021213 | 16114.8 | 0.021213 | 16114.8 | 0.021213 | 16114.8 | 0.021213 | 16114.8 | 0.021213 | 16114.8 | 0.021213 | 16114.8 | 0.021213 | 16114.8 | 0.021213 | 16114.8 | 0.021213 | 16114.8 | 0.021213 | 16114.8 | 0.021213 | 16114.8 | 0.021213 | 16114.8 | 0.021213 | 16114.8 | 0.021213 | 16114.8 | 0.021213 | 16114.8 | 0.021213 | 16114.8 | 0.021213 | 16114.8 | 0.021213 | 16114.8 | 0.021213
14622.6 | 0.021213 | 14622.6 | 0.021213 | 14622.6 | 0.021213 | 14622.6 | 0.021213 | 14622.6 | 0.021213 | 14622.6 | 0.021213 | 14622.6 | 0.021213 | 14622.6 | 0.021213 | 14622.6 | 0.021213 | 14622.6 | 0.021213 | 14622.6 | 0.021213 | 14622.6 | 0.021213 | 14622.6 | 0.021213 | 14622.6 | 0.021213 | 14622.6 | 0.021213 | 14622.6 | 0.021213 | 14622.6 | 0.021213 | 14622.6 | 0.021213 | 14622.6 | 0.021213 | 14622.6 | 0.021213 | 14622.6 | 0.021213 | 14622.6 | 0.021213 | 14622.6 | 0.021213 | 14622.6 | 0.021213 | 14622.6 | 0.021213 | 14622.6 | 0.021213 | 14622.6 | 0.021213
14320.1 | 0.023825 | 12436.1 | 0.021213 | 14320.1 | 0.023825 | 12436.1 | 0.021213 | 14320.1 | 0.023825 | 12436.1 | 0.021213 | 14320.1 | 0.023825 | 12436.1 | 0.021213 | 14320.1 | 0.023825 | 12436.1 | 0.021213 | 14320.1 | 0.023825 | 12436.1 | 0.021213 | 14320.1 | 0.023825 | 12436.1 | 0.021213 | 14320.1 | 0.023825 | 12436.1 | 0.021213 | 14320.1 | 0.023825 | 12436.1 | 0.021213 | 14320.1 | 0.023825 | 12436.1 | 0.021213 | 14320.1 | 0.023825 | 12436.1 | 0.021213 | 14320.1 | 0.023825 | 12436.1 | 0.021213 | 14320.1 | 0.023825 | 12436.1 | 0.021213 | 14320.1 | 0.023825
14171.3 | 0.025635 | 12115.5 | 0.025104 | 14171.3 | 0.025635 | 12115.5 | 0.025104 | 14171.3 | 0.025635 | 12115.5 | 0.025104 | 14171.3 | 0.025635 | 12115.5 | 0.025104 | 14171.3 | 0.025635 | 12115.5 | 0.025104 | 14171.3 | 0.025635 | 12115.5 | 0.025104 | 14171.3 | 0.025635 | 12115.5 | 0.025104 | 14171.3 | 0.025635 | 12115.5 | 0.025104 | 14171.3 | 0.025635 | 12115.5 | 0.025104 | 14171.3 | 0.025635 | 12115.5 | 0.025104 | 14171.3 | 0.025635 | 12115.5 | 0.025104 | 14171.3 | 0.025635 | 12115.5 | 0.025104 | 14171.3 | 0.025635 | 12115.5 | 0.025104 | 14171.3 | 0.025635
11319.9 | 0.026452 | 9428.28 | 0.025635 | 11319.9 | 0.026452 | 9428.28 | 0.025635 | 11319.9 | 0.026452 | 9428.28 | 0.025635 | 11319.9 | 0.026452 | 9428.28 | 0.025635 | 11319.9 | 0.026452 | 9428.28 | 0.025635 | 11319.9 | 0.026452 | 9428.28 | 0.025635 | 11319.9 | 0.026452 | 9428.28 | 0.025635 | 11319.9 | 0.026452 | 9428.28 | 0.025635 | 11319.9 | 0.026452 | 9428.28 | 0.025635 | 11319.9 | 0.026452 | 9428.28 | 0.025635 | 11319.9 | 0.026452 | 9428.28 | 0.025635 | 11319.9 | 0.026452 | 9428.28 | 0.025635 | 11319.9 | 0.026452 | 9428.28 | 0.025635 | 11319.9 | 0.026452
8672.2 | 0.027872 | 7073.59 | 0.02673 | 8672.2 | 0.027872 | 7073.59 | 0.02673 | 8672.2 | 0.027872 | 7073.59 | 0.02673 | 8672.2 | 0.027872 | 7073.59 | 0.02673 | 8672.2 | 0.027872 | 7073.59 | 0.02673 | 8672.2 | 0.027872 | 7073.59 | 0.02673 | 8672.2 | 0.027872 | 7073.59 | 0.02673 | 8672.2 | 0.027872 | 7073.59 | 0.02673 | 8672.2 | 0.027872 | 7073.59 | 0.02673 | 8672.2 | 0.027872 | 7073.59 | 0.02673 | 8672.2 | 0.027872 | 7073.59 | 0.02673 | 8672.2 | 0.027872 | 7073.59 | 0.02673 | 8672.2 | 0.027872 | 7073.59 | 0.02673 | 8672.2 | 0.027872
7036.73 | 0.029215 | 5036.83 | 0.027872 | 7036.73 | 0.029215 | 5036.83 | 0.027872 | 7036.73 | 0.029215 | 5036.83 | 0.027872 | 7036.73 | 0.029215 | 5036.83 | 0.027872 | 7036.73 | 0.029215 | 5036.83 | 0.027872 | 7036.73 | 0.029215 | 5036.83 | 0.027872 | 7036.73 | 0.029215 | 5036.83 | 0.027872 | 7036.73 | 0.029215 | 5036.83 | 0.027872 | 7036.73 | 0.029215 | 5036.83 | 0.027872 | 7036.73 | 0.029215 | 5036.83 | 0.027872 | 7036.73 | 0.029215 | 5036.83 | 0.027872 | 7036.73 | 0.029215 | 5036.83 | 0.027872 | 7036.73 | 0.029215 | 5036.83 | 0.027872 | 7036.73 | 0.029215
7036.73 | 0.035901 | 3931.96 | 0.028761 | 7036.73 | 0.035901 | 3931.96 | 0.028761 | 7036.73 | 0.035901 | 3931.96 | 0.028761 | 7036.73 | 0.035901 | 3931.96 | 0.028761 | 7036.73 | 0.035901 | 3931.96 | 0.028761 | 7036.73 | 0.035901 | 3931.96 | 0.028761 | 7036.73 | 0.035901 | 3931.96 | 0.028761 | 7036.73 | 0.035901 | 3931.96 | 0.028761 | 7036.73 | 0.035901 | 3931.96 | 0.028761 | 7036.73 | 0.035901 | 3931.96 | 0.028761 | 7036.73 | 0.035901 | 3931.96 | 0.028761 | 7036.73 | 0.035901 | 3931.96 | 0.028761 | 7036.73 | 0.035901 | 3931.96 | 0.028761 | 7036.73 | 0.035901
7036.73 | 0.038952 | 3931.96 | 0.036583 | 7036.73 | 0.038952 | 3931.96 | 0.036583 | 7036.73 | 0.038952 | 3931.96 | 0.036583 | 7036.73 | 0.038952 | 3931.96 | 0.036583 | 7036.73 | 0.038952 | 3931.96 | 0.036583 | 7036.73 | 0.038952 | 3931.96 | 0.036583 | 7036.73 | 0.038952 | 3931.96 | 0.036583 | 7036.73 | 0.038952 | 3931.96 | 0.036583 | 7036.73 | 0.038952 | 3931.96 | 0.036583 | 7036.73 | 0.038952 | 3931.96 | 0.036583 | 7036.73 | 0.038952 | 3931.96 | 0.036583 | 7036.73 | 0.038952 | 3931.96 | 0.036583 | 7036.73 | 0.038952 | 3931.96 | 0.036583 | 7036.73 | 0.038952
7036.73 | 0.041044 | 3931.96 | 0.04663 | 7036.73 | 0.041044 | 3931.96 | 0.04663 | 7036.73 | 0.041044 | 3931.96 | 0.04663 | 7036.73 | 0.041044 | 3931.96 | 0.04663 | 7036.73 | 0.041044 | 3931.96 | 0.04663 | 7036.73 | 0.041044 | 3931.96 | 0.04663 | 7036.73 | 0.041044 | 3931.96 | 0.04663 | 7036.73 | 0.041044 | 3931.96 | 0.04663 | 7036.73 | 0.041044 | 3931.96 | 0.04663 | 7036.73 | 0.041044 | 3931.96 | 0.04663 | 7036.73 | 0.041044 | 3931.96 | 0.04663 | 7036.73 | 0.041044 | 3931.96 | 0.04663 | 7036.73 | 0.041044 | 3931.96 | 0.04663 | 7036.73 | 0.041044
7036.73 | 0.045095 | 3931.96 | 0.069315 | 7036.73 | 0.045095 | 3931.96 | 0.069315 | 7036.73 | 0.045095 | 3931.96 | 0.069315 | 7036.73 | 0.045095 | 3931.96 | 0.069315 | 7036.73 | 0.045095 | 3931.96 | 0.069315 | 7036.73 | 0.045095 | 3931.96 | 0.069315 | 7036.73 | 0.045095 | 3931.96 | 0.069315 | 7036.73 | 0.045095 | 3931.96 | 0.069315 | 7036.73 | 0.045095 | 3931.96 | 0.069315 | 7036.73 | 0.045095 | 3931.96 | 0.069315 | 7036.73 | 0.045095 | 3931.96 | 0.069315 | 7036.73 | 0.045095 | 3931.96 | 0.069315 | 7036.73 | 0.045095 | 3931.96 | 0.069315 | 7036.73 | 0.045095
7036.73 | 0.051501 | 3931.96 | 0.096164 | 7036.73 | 0.051501 | 3931.96 | 0.096164 | 7036.73 | 0.051501 | 3931.96 | 0.096164 | 7036.73 | 0.051501 | 3931.96 | 0.096164 | 7036.73 | 0.051501 | 3931.96 | 0.096164 | 7036.73 | 0.051501 | 3931.96 | 0.096164 | 7036.73 | 0.051501 | 3931.96 | 0.096164 | 7036.73 | 0.051501 | 3931.96 | 0.096164 | 7036.73 | 0.051501 | 3931.96 | 0.096164 | 7036.73 | 0.051501 | 3931.96 | 0.096164 | 7036.73 | 0.051501 | 3931.96 | 0.096164 | 7036.73 | 0.051501 | 3931.96 | 0.096164 | 7036.73 | 0.051501 | 3931.96 | 0.096164 | 7036.73 | 0.051501
7036.73 | 0.065235 | 3931.96 | 0.1236 | 7036.73 | 0.065235 | 3931.96 | 0.1236 | 7036.73 | 0.065235 | 3931.96 | 0.1236 | 7036.73 | 0.065235 | 3931.96 | 0.1236 | 7036.73 | 0.065235 | 3931.96 | 0.1236 | 7036.73 | 0.065235 | 3931.96 | 0.1236 | 7036.73 | 0.065235 | 3931.96 | 0.1236 | 7036.73 | 0.065235 | 3931.96 | 0.1236 | 7036.73 | 0.065235 | 3931.96 | 0.1236 | 7036.73 | 0.065235 | 3931.96 | 0.1236 | 7036.73 | 0.065235 | 3931.96 | 0.1236 | 7036.73 | 0.065235 | 3931.96 | 0.1236 | 7036.73 | 0.065235 | 3931.96 | 0.1236 | 7036.73 | 0.065235
7036.73 | 0.076557 | 3931.96 | 0.86849 | 7036.73 | 0.076557 | 3931.96 | 0.13538 | 7036.73 | 0.076557 | 3931.96 | 0.24911 | 7036.73 | 0.076557 | 3931.96 | 0.4536 | 7036.73 | 0.076557 | 3931.96 | 0.86849 | 7036.73 | 0.076557 | 3931.96 | 0.13538 | 7036.73 | 0.076557 | 3931.96 | 0.24911 | 7036.73 | 0.076557 | 3931.96 | 0.4536 | 7036.73 | 0.076557 | 3931.96 | 0.86849 | 7036.73 | 0.076557 | 3931.96 | 0.13538 | 7036.73 | 0.076557 | 3931.96 | 0.24911 | 7036.73 | 0.076557 | 3931.96 | 0.4536 | 7036.73 | 0.076557 | 3931.96 | 0.86849 | 7036.73 | 0.076557
7036.73 | 0.081943 | 3541.85 | 0.95722 | 7036.73 | 0.081943 | 3421.8 | 0.15284 | 7036.73 | 0.081943 | 3316.2 | 0.29081 | 7036.73 | 0.081943 | 3635.59 | 0.48959 | 7036.73 | 0.081943 | 3541.85 | 0.95722 | 7036.73 | 0.081943 | 3421.8 | 0.15284 | 7036.73 | 0.081943 | 3316.2 | 0.29081 | 7036.73 | 0.081943 | 3635.59 | 0.48959 | 7036.73 | 0.081943 | 3541.85 | 0.95722 | 7036.73 | 0.081943 | 3421.8 | 0.15284 | 7036.73 | 0.081943 | 3316.2 | 0.29081 | 7036.73 | 0.081943 | 3635.59 | 0.48959 | 7036.73 | 0.081943 | 3541.85 | 0.95722 | 7036.73 | 0.081943
7036.73 | 0.087433 | 3177.13 | 1.0672 | 7036.73 | 0.087433 | 2987.18 | 0.17383 | 7036.73 | 0.087433 | 2949.96 | 0.32627 | 7036.73 | 0.087433 | 3210.51 | 0.55102 | 7036.73 | 0.087433 | 3177.13 | 1.0672 | 7036.73 | 0.087433 | 2987.18 | 0.17383 | 7036.73 | 0.087433 | 2949.96 | 0.32627 | 7036.73 | 0.087433 | 3210.51 | 0.55102 | 7036.73 | 0.087433 | 3177.13 | 1.0672 | 7036.73 | 0.087433 | 2987.18 | 0.17383 | 7036.73 | 0.087433 | 2949.96 | 0.32627 | 7036.73 | 0.087433 | 3210.51 | 0.55102 | 7036.73 | 0.087433 | 3177.13 | 1.0672 | 7036.73 | 0.087433
7036.73 | 0.28899 | 2847 | 1.1936 | 7036.73 | 0.54585 | 2577.97 | 0.19936 | 7036.73 | 0.090409 | 2599.61 | 0.36952 | 7036.73 | 0.15575 | 2791.04 | 0.63458 | 7036.73 | 0.28899 | 2847 | 1.1936 | 7036.73 | 0.54585 | 2577.97 | 0.19936 | 7036.73 | 0.090409 | 2599.61 | 0.36952 | 7036.73 | 0.15575 | 2791.04 | 0.63458 | 7036.73 | 0.28899 | 2847 | 1.1936 | 7036.73 | 0.54585 | 2577.97 | 0.19936 | 7036.73 | 0.090409 | 2599.61 | 0.36952 | 7036.73 | 0.15575 | 2791.04 | 0.63458 | 7036.73 | 0.28899 | 2847 | 1.1936 | 7036.73 | 0.54585
6201.01 | 0.31192 | 2569.9 | 1.3211 | 6072.76 | 0.60604 | 2176.52 | 0.23765 | 5928.56 | 0.10017 | 2274.17 | 0.42202 | 6098.2 | 0.17292 | 2459.56 | 0.72247 | 6201.01 | 0.31192 | 2569.9 | 1.3211 | 6072.76 | 0.60604 | 2176.52 | 0.23765 | 5928.56 | 0.10017 | 2274.17 | 0.42202 | 6098.2 | 0.17292 | 2459.56 | 0.72247 | 6201.01 | 0.31192 | 2569.9 | 1.3211 | 6072.76 | 0.60604 | 2176.52 | 0.23765 | 5928.56 | 0.10017 | 2274.17 | 0.42202 | 6098.2 | 0.17292 | 2459.56 | 0.72247 | 6201.01 | 0.31192 | 2569.9 | 1.3211 | 6072.76 | 0.60604
5436.06 | 0.34487 | 2274.17 | 1.5151 | 5273.81 | 0.67852 | 1864.67 | 0.2789 | 5213.54 | 0.10948 | 2029.36 | 0.47496 | 5340.35 | 0.19179 | 2124.84 | 0.84343 | 5436.06 | 0.34487 | 2274.17 | 1.5151 | 5273.81 | 0.67852 | 1864.67 | 0.2789 | 5213.54 | 0.10948 | 2029.36 | 0.47496 | 5340.35 | 0.19179 | 2124.84 | 0.84343 | 5436.06 | 0.34487 | 2274.17 | 1.5151 | 5273.81 | 0.67852 | 1864.67 | 0.2789 | 5213.54 | 0.10948 | 2029.36 | 0.47496 | 5340.35 | 0.19179 | 2124.84 | 0.84343 | 5436.06 | 0.34487 | 2274.17 | 1.5151 | 5273.81 | 0.67852
4755.53 | 0.38612 | 2020.9 | 1.7105 | 4642.61 | 0.75097 | 1641.49 | 0.32187 | 4499.33 | 0.12143 | 1780.88 | 0.54528 | 4681.58 | 0.21383 | 1880.32 | 0.96325 | 4755.53 | 0.38612 | 2020.9 | 1.7105 | 4642.61 | 0.75097 | 1641.49 | 0.32187 | 4499.33 | 0.12143 | 1780.88 | 0.54528 | 4681.58 | 0.21383 | 1880.32 | 0.96325 | 4755.53 | 0.38612 | 2020.9 | 1.7105 | 4642.61 | 0.75097 | 1641.49 | 0.32187 | 4499.33 | 0.12143 | 1780.88 | 0.54528 | 4681.58 | 0.21383 | 1880.32 | 0.96325 | 4755.53 | 0.38612 | 2020.9 | 1.7105 | 4642.61 | 0.75097
4164.55 | 0.43274 | 1745.87 | 2.0242 | 4173.26 | 0.82597 | 1524.12 | 0.3485 | 4082.68 | 0.13161 | 1544.97 | 0.64126 | 4147.18 | 0.23865 | 1670.91 | 1.1058 | 4164.55 | 0.43274 | 1745.87 | 2.0242 | 4173.26 | 0.82597 | 1524.12 | 0.3485 | 4082.68 | 0.13161 | 1544.97 | 0.64126 | 4147.18 | 0.23865 | 1670.91 | 1.1058 | 4164.55 | 0.43274 | 1745.87 | 2.0242 | 4173.26 | 0.82597 | 1524.12 | 0.3485 | 4082.68 | 0.13161 | 1544.97 | 0.64126 | 4147.18 | 0.23865 | 1670.91 | 1.1058 | 4164.55 | 0.43274 | 1745.87 | 2.0242 | 4173.26 | 0.82597
3931.96 | 0.4536 | 1548.2 | 2.3264 | 3931.96 | 0.86849 | 1360.06 | 0.39884 | 3931.96 | 0.13538 | 1370.04 | 0.73236 | 3931.96 | 0.24911 | 1469.39 | 1.2762 | 3931.96 | 0.4536 | 1548.2 | 2.3264 | 3931.96 | 0.86849 | 1360.06 | 0.39884 | 3931.96 | 0.13538 | 1370.04 | 0.73236 | 3931.96 | 0.24911 | 1469.39 | 1.2762 | 3931.96 | 0.4536 | 1548.2 | 2.3264 | 3931.96 | 0.86849 | 1360.06 | 0.39884 | 3931.96 | 0.13538 | 1370.04 | 0.73236 | 3931.96 | 0.24911 | 1469.39 | 1.2762 | 3931.96 | 0.4536 | 1548.2 | 2.3264 | 3931.96 | 0.86849
3635.59 | 0.48959 | 1406.3 | 2.6155 | 3541.85 | 0.95722 | 1206.06 | 0.45503 | 3421.8 | 0.15284 | 1206.06 | 0.84608 | 3316.2 | 0.29081 | 1312.59 | 1.4637 | 3635.59 | 0.48959 | 1406.3 | 2.6155 | 3541.85 | 0.95722 | 1206.06 | 0.45503 | 3421.8 | 0.15284 | 1206.06 | 0.84608 | 3316.2 | 0.29081 | 1312.59 | 1.4637 | 3635.59 | 0.48959 | 1406.3 | 2.6155 | 3541.85 | 0.95722 | 1206.06 | 0.45503 | 3421.8 | 0.15284 | 1206.06 | 0.84608 | 3316.2 | 0.29081 | 1312.59 | 1.4637 | 3635.59 | 0.48959 | 1406.3 | 2.6155 | 3541.85 | 0.95722
3210.51 | 0.55102 | 1292.17 | 2.9099 | 3177.13 | 1.0672 | 1083 | 0.52404 | 2987.18 | 0.17383 | 968.447 | 1.0932 | 2949.96 | 0.32627 | 1206.06 | 1.6183 | 3210.51 | 0.55102 | 1292.17 | 2.9099 | 3177.13 | 1.0672 | 1083 | 0.52404 | 2987.18 | 0.17383 | 968.447 | 1.0932 | 2949.96 | 0.32627 | 1206.06 | 1.6183 | 3210.51 | 0.55102 | 1292.17 | 2.9099 | 3177.13 | 1.0672 | 1206.06 | 1000 | 2987.18 | 0.17383 | 1206.06 | 1000 | 2949.96 | 0.32627 | 1206.06 | 1.6183 | 3210.51 | 0.55102 | 1292.17 | 2.9099 | 3177.13 | 1.0672
2791.04 | 0.63458 | 1206.06 | 3.154 | 2847 | 1.1936 | 979.642 | 0.58793 | 2577.97 | 0.19936 | 894.515 | 1.1986 | 2599.61 | 0.36952 | 1070.63 | 1.8774 | 2791.04 | 0.63458 | 1206.06 | 3.154 | 2847 | 1.1936 | 979.642 | 0.58793 | 2577.97 | 0.19936 | 894.515 | 1.1986 | 2599.61 | 0.36952 | 1070.63 | 1.8774 | 2791.04 | 0.63458 | 1206.06 | 3.154 | 2847 | 1.1936 |  |  | 2577.97 | 0.19936 |  |  | 2599.61 | 0.36952 | 1206.06 | 1000 | 2791.04 | 0.63458 | 1206.06 | 3.154 | 2847 | 1.1936
2459.56 | 0.72247 | 1077.36 | 3.6476 | 2569.9 | 1.3211 | 894.515 | 0.66586 | 2176.52 | 0.23765 | 722.794 | 1.5634 | 2274.17 | 0.42202 | 981.692 | 2.0909 | 2459.56 | 0.72247 | 1077.36 | 3.6476 | 2569.9 | 1.3211 | 894.515 | 0.66586 | 2176.52 | 0.23765 | 894.515 | 1000 | 2274.17 | 0.42202 | 981.692 | 2.0909 | 2459.56 | 0.72247 | 1077.36 | 3.6476 | 2569.9 | 1.3211 |  |  | 2176.52 | 0.23765 |  |  | 2274.17 | 0.42202 |  |  | 2459.56 | 0.72247 | 1206.06 | 1000 | 2569.9 | 1.3211
2124.84 | 0.84343 | 980.666 | 4.1354 | 2274.17 | 1.5151 | 786.632 | 0.77897 | 1864.67 | 0.2789 | 663.443 | 1.7375 | 2029.36 | 0.47496 | 894.515 | 2.3434 | 2124.84 | 0.84343 | 980.666 | 4.1354 | 2274.17 | 1.5151 | 894.515 | 1000 | 1864.67 | 0.2789 |  |  | 2029.36 | 0.47496 | 894.515 | 2.3434 | 2124.84 | 0.84343 | 980.666 | 4.1354 | 2274.17 | 1.5151 |  |  | 1864.67 | 0.2789 |  |  | 2029.36 | 0.47496 |  |  | 2124.84 | 0.84343 |  |  | 2274.17 | 1.5151
1880.32 | 0.96325 | 894.515 | 4.6058 | 2020.9 | 1.7105 | 727.339 | 0.86487 | 1641.49 | 0.32187 | 663.443 | 1000 | 1780.88 | 0.54528 | 789.101 | 2.7588 | 1880.32 | 0.96325 | 894.515 | 4.6058 | 2020.9 | 1.7105 |  |  | 1641.49 | 0.32187 |  |  | 1780.88 | 0.54528 | 894.515 | 1000 | 1880.32 | 0.96325 | 894.515 | 4.6058 | 2020.9 | 1.7105 |  |  | 1641.49 | 0.32187 |  |  | 1780.88 | 0.54528 |  |  | 1880.32 | 0.96325 |  |  | 2020.9 | 1.7105
1670.91 | 1.1058 | 783.351 | 5.5079 | 1745.87 | 2.0242 | 663.443 | 0.97134 | 1524.12 | 0.3485 |  |  | 1544.97 | 0.64126 | 722.794 | 3.0887 | 1670.91 | 1.1058 | 783.351 | 5.5079 | 1745.87 | 2.0242 |  |  | 1524.12 | 0.3485 |  |  | 1544.97 | 0.64126 |  |  | 1670.91 | 1.1058 | 894.515 | 1000 | 1745.87 | 2.0242 |  |  | 1524.12 | 0.3485 |  |  | 1544.97 | 0.64126 |  |  | 1670.91 | 1.1058 |  |  | 1745.87 | 2.0242
1469.39 | 1.2762 | 716.777 | 6.1924 | 1548.2 | 2.3264 | 663.443 | 1000 | 1360.06 | 0.39884 |  |  | 1370.04 | 0.73236 | 663.443 | 3.4762 | 1469.39 | 1.2762 | 716.777 | 6.1924 | 1548.2 | 2.3264 |  |  | 1360.06 | 0.39884 |  |  | 1370.04 | 0.73236 |  |  | 1469.39 | 1.2762 |  |  | 1548.2 | 2.3264 |  |  | 1360.06 | 0.39884 |  |  | 1370.04 | 0.73236 |  |  | 1469.39 | 1.2762 |  |  | 1548.2 | 2.3264
1312.59 | 1.4637 | 663.443 | 6.904 | 1406.3 | 2.6155 |  |  | 1206.06 | 0.45503 |  |  | 1206.06 | 0.84608 | 663.443 | 1000 | 1312.59 | 1.4637 | 663.443 | 6.904 | 1406.3 | 2.6155 |  |  | 1206.06 | 0.45503 |  |  | 1206.06 | 0.84608 |  |  | 1312.59 | 1.4637 |  |  | 1406.3 | 2.6155 |  |  | 1206.06 | 0.45503 |  |  | 1206.06 | 0.84608 |  |  | 1312.59 | 1.4637 |  |  | 1406.3 | 2.6155
1206.06 | 1.6183 | 587.711 | 8.0853 | 1292.17 | 2.9099 |  |  | 1083 | 0.52404 |  |  | 968.447 | 1.0932 |  |  | 1206.06 | 1.6183 | 663.443 | 1000 | 1292.17 | 2.9099 |  |  | 1083 | 0.52404 |  |  | 968.447 | 1.0932 |  |  | 1206.06 | 1.6183 |  |  | 1292.17 | 2.9099 |  |  | 1206.06 | 1000 |  |  | 1206.06 | 1000 |  |  | 1206.06 | 1.6183 |  |  | 1292.17 | 2.9099
1070.63 | 1.8774 | 540.58 | 9.1474 | 1206.06 | 3.154 |  |  | 979.642 | 0.58793 |  |  | 894.515 | 1.1986 |  |  | 1070.63 | 1.8774 |  |  | 1206.06 | 3.154 |  |  | 979.642 | 0.58793 |  |  | 894.515 | 1.1986 |  |  | 1070.63 | 1.8774 |  |  | 1206.06 | 3.154 | [10 empty] | 1206.06 | 1000 |  |  | 1206.06 | 3.154
981.692 | 2.0909 | 489.497 | 10.4797 | 1077.36 | 3.6476 |  |  | 894.515 | 0.66586 |  |  | 722.794 | 1.5634 |  |  | 981.692 | 2.0909 |  |  | 1077.36 | 3.6476 |  |  | 894.515 | 0.66586 |  |  | 894.515 | 1000 |  |  | 981.692 | 2.0909 |  |  | 1077.36 | 3.6476 | [14 empty] | 1206.06 | 1000
894.515 | 2.3434 | 437.718 | 12.2599 | 980.666 | 4.1354 |  |  | 786.632 | 0.77897 |  |  | 663.443 | 1.7375 |  |  | 894.515 | 2.3434 |  |  | 980.666 | 4.1354 |  |  | 894.515 | 1000 | [6 empty] | 894.515 | 2.3434 |  |  | 980.666 | 4.1354
789.101 | 2.7588 | 437.718 | 1000 | 894.515 | 4.6058 |  |  | 727.339 | 0.86487 |  |  | 663.443 | 1000 |  |  | 789.101 | 2.7588 |  |  | 894.515 | 4.6058 | [10 empty] | 894.515 | 1000 |  |  | 894.515 | 4.6058
722.794 | 3.0887 |  |  | 783.351 | 5.5079 |  |  | 663.443 | 0.97134 | [6 empty] | 722.794 | 3.0887 |  |  | 783.351 | 5.5079 | [14 empty] | 894.515 | 1000
663.443 | 3.4762 |  |  | 716.777 | 6.1924 |  |  | 663.443 | 1000 | [6 empty] | 663.443 | 3.4762 |  |  | 716.777 | 6.1924
586.484 | 4.0795 |  |  | 663.443 | 6.904 | [10 empty] | 663.443 | 1000 |  |  | 663.443 | 6.904
527.193 | 4.6786 |  |  | 587.711 | 8.0853 | [14 empty] | 663.443 | 1000
490.009 | 5.1837 |  |  | 540.58 | 9.1474
437.718 | 6.0515 |  |  | 489.497 | 10.4797
437.718 | 1000 |  |  | 437.718 | 12.2599
|  |  |  | 437.718 | 1000